## Slide 1: Optimization
Master Course
2025-06-02

## Slide 2: Optimization
Single and multi-variate
Single and multi-objective
Constrained and unconstrained
Overview

## Slide 3: Cascaded Heat Pump
Heat source
  Fluid: air
  Temperature: 20 °C
  Pressure: 1 bar
Heat sink
  Fluid: water
  Saturated liquid at inlet, saturated vapor at outlet
  Temperature: 110 °C
Cycle
  Working fluids: R245FA (lower), R1233zd(E) (upper)
  Evaporator outlets: saturated vapor
  Condenser outlets: saturated liquid
  Condensation temperature: 60 °C
Components
  Compressor efficiency: 80 %
  Heat exchanger minimal pinch: 10 K
  Disregard pressure drops in heat exchangers
Build a heat pump model with the following specifications

## Slide 4: Heat pump: Single-variate optimization
Implement a method, which allows you to maximize the COP of the heat pump
  Think about which decision variable should be taken into consideration.
  Use a custom method for this (think about the third lecture)!
  Implement a method using scipy
  Restructure your code in the way necessary for the tespy-pygmo integration
Tasks

## Slide 5: Heat pump: advanced optimization
Use the tespy-pygmo integration for all upcoming tasks
Simultaneously optimize the
  lower cycle condensation temperature
  minimal pinch of all heat exchangers
Run a multi-objective optimization to maximize COP and minimize the total heat exchange area
Tasks

## Slide 6: Simple ORC
Heat source
  100 kg/s of air
  Temperature: 160 °C
  Pressure: 1 bar
Heat sink
  Fluid: air
  Temperature: 20 °C, air temperature increase: 15 K
  Pressure: 1 bar
Cycle
  Working fluid: water
  Condenser outlet: saturated liquid
  Evaporator inlet: saturated liquid
  Evaporator outlet: saturated gas, 140 °C
Components
  Pump efficiency: 75 %
  Turbine efficiency: 85 %
  Evaporator lower terminal temperature diff: 5 K
  Condenser lower terminal temperature diff: 15 K
  Disregard pressure drops in heat exchangers
Build an ORC model with the following specifications

## Slide 7: Simple ORC: Single-variate optimization
Implement a method, which allows you to maximize the power output of the plant
  Think about which decision variable should be taken into consideration.
  Use a custom method for this (think about the third lecture)!
  Implement a method using scipy
  Restructure your code in the way necessary for the tespy-pygmo integration
Tasks

## Slide 8: Simple ORC: advanced optimization
Use the tespy-pygmo integration for all upcoming tasks
Implement a lower limit for the air discharge temperature, how do the results change?
Simultaneously optimize the
  turbine inlet temperature
  evaporator minimal pinch
  preheater approach temperature difference
Run a multi-objective optimization to maximize power output and minimize the total heat exchange area
Tasks

## Slide 9: Next Time: Exam preparation
Your questions on all of the lectures, scripts, methods, … we implemented
Things to prepare